# Building Electrical Design Notes and Guidelines

This is about design, material selection, and installation of electrical systems in plant buildings and commercial buildings. This article is for electrical installations in non-hazardous areas. For electrical installation. Main keywords for this article are Building Electrical Design Notes, Building Electrical Testing, Building Electrical Installation, Building Electrical Wiring Methods, Insulation Resistance Test.

Building Electrical Design References
National Electrical Manufacturer Association (NEMA)
C80.1 Rigid Steel Conduit – Zinc Coated (GRC)
C80.3 Electrical Metallic Tubing – Zinc Coated (EMT)
WC 7 Cross-Linked-Thermosetting-Polyethylene-Insulated Wire and Cable for theTransmission and Distribution of Electrical Energy (ICEA S-66-524)
WD 6 Wiring Devices- Dimensional Requirements
National Fire Protection Association (NFPA)
70 National Electrical Code, 2008
780 Standard for the Installation of Lightning Protection Systems
International Electrical Testing Association (NETA)
ATS- Acceptance Testing Specifications for Electric Power Distribution Equipment and Systems
Underwriters Laboratories (UL)
4 UL Standard for Safety Armored Cable

### What is Busway.

Busways are an assembly of factory-mounted, bare or insulated conductors, which are usually copper or aluminum bars, rods, or tubes installed in a grounded metal enclosure.

### What is Wireway.

Wireways are metallic or nonmetallic troughs with covers for housing and protecting wires and cables.

## Building Electrical Design Notes and Guidelines

- Lighting and receptacle circuit wiring shall comply with Lighting and Receptacle Circuit Wiring Requirements, and NFPA 70.

- Lighting circuits shall support lighting systems designed in accordance with Lighting Design Requirements in Process Industry and light fixtures in accordance with Lamp Selection and Applications & Lighting Fixture Selection and Applications.

- Battery rooms shall comply with Battery Room Design Requirements.

- Installation, inspection and testing of electrical systems in buildings, shall conform to international standards which you can navigate in PAKTECHPOINT.COM.

## Building Electrical Installation

- All work shall be performed by skilled personnel.

- Drilling of holes in flanges of structural members, for mounting small electric and equipment items, shall conform to Field Drilling of Holes in Structural Steel.

- Where the corrosion protective finish is removed from any equipment or material by, for example, cutting or welding or by accidental damage, the original finish shall be restored.

- Welding to structures, beams, or equipment which have been stress relieved (heat treated after fabrication) shall not be permitted.

- The installation of, for example, supports, brackets, and hangers for equipment and materials, shall not weaken the structure to which they are attached.

- All fastening hardware, for example bolts, nuts, screws, and washers, shall be stainless steel for outdoor use and zinc plated for indoor use. Supports for conduit and equipment shall be hot dipped galvanized steel.

- Interface wiring to all electrical equipment shall be connected in accordance with equipment specifications and manufacturer’s instructions.

- All components, equipment, and materials of the same size, rating, and configuration shall be supplied by one manufacturer, and shall be interchangeable.

## Building Electrical Power Supply Requirements

- Process control buildings, commercial buildings and substations shall have a normal and an essential power source. Both power sources shall be 480 V, 3 phase, and high resistance grounded (3 wire).

- The building power requirements are 480 V, 3 phase, 4 wire. In some cases a small substation may be required.

- If the load is small or the building is close to a substation, the building can be served with a 480 V feeder from a substation.

- Where a building is fed from a substation, contractor shall provide the conversion from a three-wire system to a four-wire system.

- These buildings shall have an essential power supply for essential loads and an uninterruptible power supply (UPS) as an alternative power supply. The UPS shall be on the essential power supply.

- Work shops, operator shelters, and other small buildings shall be served from a nearby 480 V source. The source can be a substation or another building. The building being served shall have a 480 V main panel as required by NFPA 70 Article 230. Ground fault protection shall be provided where required by NFPA 70. These buildings shall have an essential power supply for essential lights and where UPS systems are installed, there shall be an essential power supply for the UPS alternative power.

- All building air conditioning (A/C) equipment, for example fans, blowers, compressors, and condensers, shall be served from the building motor control centers (MCC). Wiring shall also be provided for A/C system controls, and an interface with the building fire alarm system.

## Distribution Equipment

- Lighting loads shall be on separate transformers and panelboards from nonlighting loads.

- Receptacle circuits shall be on separate transformers and panelboards from non-receptacle circuits.

- For operator shelters and other small buildings, the lighting circuits and receptacle circuits may be combined on a single transformer and panelboard.

## Motor Control Centers and Switchboard

The main service entrance equipment for large buildings and buildings with three phase loads shall consist of a MCC, or switchboard with main breakers and motor starters, or both. MCC’s and switchboards shall comply with Electrical System Design Criteria.

## Transformers

- Step-down dry type power transformers provided to serve buildings constructed in accordance with this standard shall be in accordance with Dry Type Transformer. The primary supply shall be 13.8 kV or 4.16 kV, 3 phase, 60 Hz, low resistance grounded. The secondary system voltage shall be 480/277 V, 3 phase, 60 Hz, solidly grounded. Changing can be done on project requirement based.

- Dry type lighting and distribution transformers for building lighting, receptacles, fans, small heating and air conditioning units, and kitchen appliances shall comply with Dry Type Distribution and Power Transformers Design Notes, Lighting and Receptacle Circuit Wiring Requirements.

- Lighting transformers shall be sized according to Lighting and Receptacle Circuit Wiring Requirements.

- Dry type transformers serving non-linear loads shall have a K-rating not less than as specified in Dry Type Distribution and Power Transformers Design Notes.

## Building Electrical Panelboards

- Panelboards shall comply with and Lighting and Receptacle Circuit Wiring Requirements.

- The circuit breakers shall be sized based on initial loading and ultimate loading according to Lighting and Receptacle Circuit Wiring Requirements.

- Panelboards shall have 20 percent spare breakers.

- The selected location of the panelboard shall minimize branch circuit lengths.

- Branch circuits supplying lighting or other devices that are switched periodically at the panelboard, shall be located in the upper portion of the panelboard. Circuits that are switched from local wall or column-mounted
switches, and those that supply receptacles and other loads that are normally continuously energized, shall be located in the lower portion of the panelboard.

- The side gutter of panelboards shall be a minimum of 114 mm wide.

- The mounting height of the panelboard shall not exceed 1980 mm from the floor to the top of the panelboard cabinet.

- Aheavy duty external grounding lug and terminal strip shall be provided.

- Neutral buses in panelboards shall be supplied with space and lugs for the connection of a separate neutral wire for each branch circuit.

Main keywords for this article are Building Electrical Design Notes, Building Electrical Testing, Building Electrical Installation, Building Electrical Wiring Methods, Insulation Resistance Test.

## Building Electrical Wiring Methods

- Wiring methods shall conform to NEC Wiring System Types & NEC Wireway Systems in Plant Industry and NFPA 70, Article 300.

- Separate neutral and ground conductors shall be provided for each branch circuit.

- Wiring methods shall be selected as follows:
a. Electrical conductors enclosed in rigid galvanized steel conduit, conduit bodies, and wireways shall be the principal wiring method
b. The use of busways and cable trays shall be limited to electrical rooms, buildings, and repair shops
c. The use of wireways shall be restricted to short runs where many electrical conductors may be collected. Wireways shall not be used as a substitute for conduit.
d. Conduit shall be electrical metallic tubing (EMT), rigid galvanized steel (RGS), or PVC coated RGS
e. The use of EMT and intermediate metal conduit shall be restricted to dry, unclassified locations, for example office buildings, and where the installation will not be subject to mechanical damage. EMT shall conform to NEMA C80.3 . Only compression type EMT connectors shall be acceptable.
f. In buildings where conduit is installed in concrete floors, PVC coated RGS conduit conforming to SES E23-S01shall be used. The minimum
size for below grade conduit shall be 1 in.
g. When above-grade conduit may be subjected to mechanical damage, or is installed outdoors in exposed locations, rigid hot dipped galvanized steel conduit shall be used. In corrosive areas, PVC coated rigid galvanized steel conduit shall be used.

- The mechanical continuity of all raceways, and the electrical continuity of metal raceways, shall be maintained throughout the electrical system.

- Spacing between instrumentation circuits and power, lighting, and control circuits in raceways and cable trays.

- See Electrical System Design Criteria for types of circuits that may be run in the same cable tray if separated by a barrier.

## Conduit and Fittings

- Conduit and fittings shall be supplied and installed in accordance with Conduit Types Conduit Fittings and Electrical Boxes and Conduit Installation Guidelines for Engineers.

- For interior walls of hollow construction, for example sheetrock covered beams, the conduit installation shall be concealed within the building wall space. For building exteriors and interior solid walls, the conduit installation may be surface mounted.

- The minimum conduit size for power feeders and multiple circuits shall be ¾ in.

- Junction boxes shall be independently mounted, and shall not rely on the mechanical support of the attached conduit for support.

## Wireways

- The wireway installation shall be concealed within the building wall space.

- Wireway shall be manufactured from galvanized sheet steel with a minimum thickness of 1.7 mm (20 gage).

- Wireway accessories shall be of the same make and type as the wireway.

- Wireway shall not contain preformed knockout stampings; required holes shall be drilled to suit the installation requirement. In the event of modification, unused holes shall be plugged.

## Cable Tray

- Cable tray shall be supplied and installed in accordance with Cable Tray Installation Guidelines for Engineers.

- Cable tray shall not be used for routing of conductors to building related electrical equipment, for example lights, receptacles, and HVAC equipment. Cable tray may be used for routing of cables to process equipment, cranes, hoist, conveyors, and other similar equipment.

## Busway

- Busways may be used to feed power to permanently installed equipment, for example lathes, drills, and presses (maintenance tools), conveyor systems, cranes, hoist, and similar equipment. Busways may also be used to provide power to isolated areas in the interior of large rooms, for example warehouse areas, large open office areas and large open areas in manufacturing buildings.

- Busways shall not be installed in the following locations:
a. Where subject to physical damage, excessive vibration, or corrosive vapors
b. Where subject to dust, unless totally enclosed
c. In any Class I, Division 1 location
d. In Class I, Division 2 locations, unless enclosed and gasketed
e. In an unclassified location above a classified location, unless totally enclosed
f. Above highly flammable materials or areas where personnel may congregate, unless totally enclosed

- Busway enclosures shall be securely fastened in place, bonded, and grounded in conformance with NFPA 70, Article 364.

- All bolted busway joints shall be assembled and torqued in conformance with vendor’s instructions.

- Busway fittings and accessories shall be readily accessible.

- Busways shall be securely supported at intervals not exceeding 1.52 m (60 in), unless otherwise designed and marked.

- Busway dead ends shall be closed.

- Busway overcurrent protection shall be in accordance with NFPA 70, Article 364.

## Wire and Cable

- All cables shall be supplied and installed in accordance with NEC IEC Based Low Voltage Cables Selection Criteria and Cables Installation, Splicing and Termination Cable Requirements.

- For all cable, construction and minimum wire sizes shall be as defined in NFPA 70, NEMA WC 7, Electrical System Design Criteria.

- Cables shall be continuous from end to end without splices.

- Permanent wire markers shall be installed on all wires at termination points.

- Composite power and control cables, where specified, shall be terminated in a way that ensures power and control leads will reach their respective termination points without splicing. Removal of the jacket for the necessary length shall be done without damaging individual conductors.

- In buildings with suspended ceilings, armored cable that complies with of UL 4 may be used for general wiring of lighting and receptacle circuits. Type ac cable shall be secured in accordance with NFPA 70 Article 333.

- The radii of cable bends shall equal or exceed the minimum values specified by manufacturer. The minimum bending radii specified in NEMA WC7 and in NFPA 70 may be used when manufacturer’s data is not available.

- Pulling tensions and sidewall pressures for wire and cable shall not exceed the maximum values specified by manufacturer.

## Junction and Pull Boxes

- Junction boxes and pull boxes shall be supplied and installed in accordance with Procedure for Instrument Junction Box Installation.

- Junction boxes shall be readily accessible.

- Junction boxes shall be independently mounted and shall not rely on the mechanical support of the attached conduit for support.

## Disconnect Switches

- Air conditioner compressor units shall have a disconnect switch located within sight of the motor. Switch shall comply with NFPA 70 Article 440.

- Electric space heating equipment shall have disconnecting means that comply with NFPA 70 Article 424.

- Electric stoves, electric water heaters, and other appliances shall have dedicated disconnecting means that comply with NFPA 70 Article 422.

## Switches and Receptacles

- Switches and receptacles and their circuits shall comply with Lighting and Receptacle Circuit Wiring Requirements and NFPA 70.

- The indoor lighting fixtures shall be controlled by one (1) or more multi-way switches located on the wall adjacent to the non-hinged side of the door frame, and spaced at least 100 mm from the door trim or corner of the room when practicable. The switch mounting height shall be 1220 mm above the finished floor.

- Local switches for lighting shall be rated 20 A, and shall be supplied with an ac rating suitable for the utilization voltage.

- Outdoor fixtures shall be controlled using photo-controlled, multi-circuit lighting contactors equipped with door mounted hand-off-automatic (HOA) switches.

- Receptacles and switches shall have external back wiring clamps with an anti rotational strand containment feature.

- Receptacle mounting height shall be:

a. 915 mm in warehouse and similar areas
b. 460 mm in offices and similar areas

- The maximum receptacle spacing as measured along each unbroken wall shall be:
a. 3.2 m between receptacles installed in offices
b. 15 m between receptacles installed in warehouse

- Receptacle spacing and mounting height for laboratory and other locations with special purpose equipment shall be as indicated on the drawings.

- Ground fault interrupter receptacles shall be installed in kitchen, restrooms, outdoor areas, and other areas which tend to be wet during operation.

- Receptacles shall be as follows:

a. Convenience receptacles shall be supplied in accordance with NFPA 70
b. Receptacle dimensions shall comply with NEMA WD 6
c. Unclassified locations shall use duplex, 2-pole, 3-wire,’U’ shaped grounding, contact type, rated 20 A, 120 V ac. These receptacles shall be installed in a box with wall plate for flush mounting, or in a box with a sheet steel cover for surface mounting.
d. In hazardous areas, receptacles shall be Crouse Hinds type CPS 152211 M6, 120 V ac, 20 A, 2 wire, 3 pole
e. In non-hazardous areas receptacles shall have a pin configuration which ensures that the plugs are not interchangeable with those in the hazardous area
f. Receptacles shall be limited to eight (8) per branch circuit. Circuit loading shall be estimated on the basis of 180 VA for each receptacle.
g. Welding receptacles shall be provided in all shop areas, positioned in a way that a receptacle may be reached by a 30 m cord from any location in the area
h. Welding receptacles shall be arranged in groups of not more than three (3) outlets per each welding circuit. The size of the welding power supply feeder shall be based upon the following total continuous load:
(i) One (1) welding receptacle: 40 kVA
(ii) Two (2) welding receptacles: 70 kVA
(iii) Three (3) welding receptacles: 90 kVA
i. Welding receptacles shall be Crouse-Hinds Type EPC-61042-WT1003-3 circuit breaker with arktite receptacle and APJ No. 10487 rated 100 A, 3wire, 4 pole plug or Appleton type EBR 1034 E100 with CHD 31006 circuit breaker and female 480 V, 3 wire, 4 pole plug.

- Receptacles should be wall mounted. Floor mounted receptacles should be avoided.

- Dedicated receptacle circuitry shall be provided for special power requirements, for example computer system circuits, separate outlets for building cleaning equipment, and kitchen appliances. In particular, office areas with computer terminals or other electronic equipment shall be wired to preclude overheating of the branch circuit panels and neutral conductors caused by harmonic currents of non-linear type loads.

## Building Electrical Design Lighting

- The lighting in buildings shall comply with the Electrical System Design Criteria, Lighting Design Requirements in Buildings, Lamp Selection and Applications & Lighting Fixture Selection and Applications, and Lighting and Receptacle Circuit Wiring Requirements.

- Rapid start fluorescent fixtures shall be used for low ceiling, indoor areas requiring high illumination levels, for example office and control rooms. The fixture ballast voltage may be 120 V or 277 V single phase. Lamps shall be color corrected, cool white.

- High pressure sodium fixtures with color corrected lamps shall be used in outdoor and indoor applications both in classified and non-classified areas where specified, and with ballast voltages of 120 V or 277 V single phase as required.

- In offices areas with suspended ceilings, drop-in flush troffers shall be used.

- Lighting for control room instrument panels and similar installations shall be designed to illuminate vertical panel mounted equipment and details with glarefree uniform intensity.

- For control room general area, a luminous ceiling metallic grid parabolic system shall be provided.

- The exterior lighting installation shall be weatherproof and listed for the area installed, if installed in a hazardous location.

- Luminaries for general illumination shall be mounted minimum 2440 mm above the finished floor.

## Special Lighting

- Lighting for control rooms with video display terminals shall be designed to minimize glare and avoid ceiling reflections on the terminal faces.

- Light sources shall be positioned out of the mirror-angle of reflection with respect to the task and the operator’s eyes.

- Recessed fluorescent luminaries with an aluminum parabolic wedge louver shall be provided.

- A luminary dimming system shall be provided for conference rooms, auditoriums, control rooms, and other rooms where the ability to adjust the lighting level is important for the activities for which the room is intended, for example the use of projectors, control system monitors, and television displays.

- Fluorescent fixtures installed in rooms with electronic equipment shall be provided with inductance-capacitance filters.

## Essential Lighting

- Substation and control room lighting shall be fed from the plant essential power system.

- Essential lighting shall be provided as follows:
a. Occupied Areas – selected key luminaries (approximately 20 percent of the fixtures) for general illumination, to permit safe access and egress by personnel and for monitoring critical local controls, shall be assigned to essential power system. These fixtures shall be marked and identified as emergency lighting.
b. All Areas – exit lights. These fixtures shall be battery pack type fixtures.

## Obstruction Lighting

Usually, aviation obstruction lighting is not required on buildings. If a building structure exceeds the height of other nearby structures, see Lighting Design Requirements in Buildings for determination of aviation obstruction lighting requirements.

## Building Electrical Design Grounding

- Grounding and lightning protection of buildings shall be in accordance with NFPA 70.

- Wall mounted, pre-fabricated, copper grounding bus-bar(s) for non-instrument grounding shall be provided in the building locations shown on the drawings, and shall be connected to the building steel and plant grounding grid as shown on the drawings.

- Grounding bus-bar units shall be fabricated from 6 mm x 51 mm x 356 mm copper bar (minimum) and as detailed on the drawings.

- Grounding bus-bar units over 1520 mm in length shall have two (2) connections to the plant grounding grid.

- All electrical equipment installed in the building shall be connected to a grounding bus-bar.
Buildings point of view grounding

- Building frames shall be connected to the main grounding loop.

- The local building grounding system shall be connected to the plant area grounding system at two locations minimum, with green insulated, 70 mm2 (#2/0 AWG) copper wire.

- Foundation bolts shall not be used for grounding purposes.

- Lightning protection shall be furnished for all buildings, in conformance with NFPA 70 and 780, and Grounding and Lightning Protection for Buildings and Substations. The facilities shall include all necessary cable, down conductors, lightning rods/air terminals, connectors, test clamps, and connections to the plant grounding system.

## Communication Systems

We will include article related soon.

## Fire Alarm Systems

We will include article related soon.

## Building Electrical Documentation

Required documentation for the electrical systems for buildings. The documentation required will vary according to the size and function of the building. The electrical documents specified in this section shall be provided.

## One Line Diagram

- Control buildings, administration buildings, and other larger buildings shall require one line diagrams to show the details of these buildings’ more complex power systems.

- The one line diagram shall show the electrical system from the electrical service to distribution panels, motors, HVAC, UPS, and battery chargers.

- Equipment numbers and ratings shall be shown.

## Equipment Location Plan

- Location of transformers, motor control centers, switchboards, panelboards, uninterruptable power supplies, batteries, battery chargers, and automatic transfer switches shall be shown. Ratings and sizes of the equipment shall be shown.

- Locations of the interconnecting busways, wireways, cable trays, and conduits shall be shown.

## Building Electrical Lighting Plan

- Locations of lighting transformers and panelboards shall be shown.

- Locations of receptacle transformers and panelboards shall be shown.

- Locations of transformers and panelboards of, for example kitchen appliances, and water heaters shall be shown.

- Locations of welding receptacles shall be shown.

- Designation of each circuit, conduit, wireway, busway, transformer, and panelboard shall be shown.

- For each conduit, wireway, busway, show:
a. Its routing
b. Its designation
c. Designations of all circuits inside
d. Number and size of conductors of each circuit

- Plan and elevation drawings shall be prepared, to determine if aviation obstruction lighting is required. If aviation obstruction lighting is required, aviation obstruction lighting plan drawings shall be prepared, showing the
lights and the essential power lighting circuits from the essential power panelboard to the lights, in accordance with Lighting Design Requirements in Buildings and Process Industry.

- Lighting calculations shall be provided.

- Installation details shall be provided.

## Communications Plan

Article will be soon for Communication systems requirements.

## Grounding Plan

- Building structure grounding shall be shown.

- Grounding for the building’s electrical system, for example panelboards, transformers, motor control centers, and switchboards shall be shown.

- Grounding for the communications systems shall be shown.

- Grounding details shall be shown.

Other Documentation

- Panelboard schedules.

- Cable schedules.

- Installation details.

- Lighting calculations.

- Test reports.

## Building Electrical Testing

The installation shall be tested upon completion of the work, as specified in NETA-ATS, and shall include the tests listed in this section.

- The installation of all wiring, cabling, terminations, conduit or raceway and device installation shall be visually checked for proper installation, and all wiring continuity shall be checked.

- All control equipment and circuits shall be checked for proper operation.

## Insulation Resistance Test

- Tests shall be carried out using a 500 V Megger tester for equipment rated 600 V.

- With all apparatus and lamps disconnected and all switches closed, the insulation resistance shall not be less than one (1) MΩ between conductors or conductors to earth.

- Where it is not practicable to disconnect the apparatus or remove lamps, with all switches open, the insulation resistance shall not be less than 0.5 MΩ between conductors or conductors to earth.

## Polarity Check

Verification of polarity shall be made, to ensure that all single pole control devices are connected to the live conductor only; that the outer contacts of center-contact bayonet and Edison-type screw lampholders are connected to the neutral or grounded conductor; and that cabling has been correctly connected to plugs and receptacles.

## Grounding

- Tracing the Sun: Dual Axis Solar Tracker System

October 27, 2017

84715

Advertisement

Solar energy is coming up as a major source of energy. The need of the hour is renewable energy resources with cheap running costs. With the current systems for solar energy harvesting, we have high production only at fixed times mostly noon. This project proposes a dual axis solar tracker system that increases the productivity by a significant margin.

- Solar Angles

The angle of inclination ranges between -90° after sun rise and +90° before sunset passing with 0° at noon. This makes the collected solar radiation to be 0% at sunrise and sunset and 100% at noon. This variation of solar radiations collection leads the photovoltaic panel to lose more than 40% of the collected energy. In this project, we take you through designing a Solar tracker so that you maximise on the solar energy collection.

- Designing the Dual Axis Solar Tracker system

This system requires involvement of a wide range of engineering including mechanical electrical and electronics. The system can be broken down into these three domains as well.

The mechanical part would involve designing a smooth gear system to move as per requirement. The electrical part would be the working of solar panel and battery requirement. The electronics would involve designing the sensor system that would generate commands for the gear system to act accordingly.

Electronics component list:

| S.No. | Component | Quantity |
| --- | --- | --- |
| 1 | Transformer step down 12-0-12 | 1 |
| 2 | Voltage Regulator 7805 | 1 |
| 3 | Transistor npn | 4 |
| 4 | Diode | 2 |
| 5 | Capacitor | 3 |
| 6 | Variable Resistor | 4 |
| 7 | Light dependent resistors (LDR) | 4 |
| 8 | Microcontroller 89S52 | 1 |
| 9 | Motor driver uln2003a | 2 |
| 10 | Solar Panel (all black) | 1 |
| 11 | Unipolar stepper motor | 2 |
| 12 | Crystal oscillator 12 Mhz | 1 |

The system employs spur gear for the implementation of the dual axis solar tracker.

Fig: A Spur Gear

A spur gear is a simplest type of gear and can be seen a lot of applications including clocks and escalators. It consists of teeth protruding perpendicular to the circumference of the wheel.

For the dual axis rotation we propose the arrangement mentioned in the diagram below.

Dual axis rotation

The system is implemented using Atmel IC AT89C51. The circuit design for the system would be:

Fig: Circuit diagramFig: PCB Layout on desktopFig: Circuit implementation of Dual axis solar tracker system

- Final Results

Dual Axis Solar Tracker project is to provide an efficient solar distributed generation system. At maximum, the solar tracker is perpendicular to the light source. The built system has a calculated annual energy gain of 48.982% compared to an immobile solar panel. Compared to a single axis tracker, the dual-axis tracker has an annual energy gain of 36.504%.
The purpose of a solar tracker is to accurately determine the position of the sun. This enables solar panels interfaced to the tracker to obtain the maximum solar radiation. With this particular solar tracker a closed-loop system was made consisting of an electrical system and a mechanical system with the help of electronics.

# 5V DC To 48V DC Converter For Phantom Power Supplies

By PETRE TZV PETROV

August 13, 2019

35983

Advertisement

This circuit presents a simple and low-cost DC-to-DC converter for phantom power supplies used in mixing consoles, microphone preamplifiers, telephone systems and similar equipment. There are many application circuits that require 24V and 48V phantom power supplies, but these DC power supplies are costly and not easily available. 5V DC power supplies are easily available at low cost. This circuit presents a solution for converting 5V DC to 48V DC using a popular MC34063A IC.

## Circuit and working

The circuit diagram of the 5V DC to 48V DC converter is shown in Fig. 1. It is built around boost/buck/inverting switching regulator MC34063A (IC1), two rectifier diodes 1N4007 (D1 and D3), Schottky diode SR1100 (D2), two 5mm LEDs (LED1 and LED2), two inductors (L1 and L2) and a few other components.

Fig. 1: Circuit diagram of 5V DC to 48V DC converter

Input power supply ranging from 5V to 7V can be applied to connector CON1. Fuse F1 protects the circuit from any continuous over-current input. Diode D1 protects the circuit from reverse input voltage. Resistor R2 limits the maximum switching current to around 1.5A, as per relationship:

Ipeakmax = 0.3V/R2

Resistor R3 limits the current for the inbuilt driver transistor of IC1. This current should be below 100mA. Operating frequency of MC34063A is in the range of 40kHz to 60kHz, and depends mainly on capacitor C3. Inductor L1 is in the range of 100µH to 150µH for current above 1.8A.

Output voltage is around 48V and can be adjusted with R4. It can be calculated using the approximate relationship:

Vout = 1.25Vx(1+R4/R5)

Output current is up to around 50mA, which is enough for several applications including microphone amplifiers. Voltage on pin 5 of IC1 should be equal to internal reference voltage or around 1.25V (1.21V to 1.29V). Schottky diode D2 should preferably be rated at least 100V. Schottky or ultrafast diode can either be SB1A0, SR1100, SS110 or SR180.

C4 and C5 are the first filtering capacitors. Ripples at OUTPUT1 are around 50mV at 50mA load, which may be too high for some applications. So, second output (OUTPUT2) is provided after LC filter. L2 (usually from 22µH to 220µH for current above 100mA) and C6 produce additional filtration of the voltage produced by the DC-to-DC converter.

We can use both the outputs, OUTPUT1 and OUTPUT2, at the same time under the condition that total current is below 60mA. The circuit does not need any adjustment.

## Construction and testing

A PCB layout of the DC-to-DC converter is shown in Fig. 2 and its components layout in Fig. 3. After assembling the circuit on the PCB, connect the 5V regulated power supply across CON1. Connect LED1 and LED2 on the front panel to indicate power status.

Fig. 2: PCB layout of DC-to-DC converterFig. 3: Components layout for the PCB

#### Download PCB and component layout PDFs: click here

Petre Tzv Petrov was a researcher and assistant professor in Technical University of Sofia (Bulgaria) and expert-lecturer in OFPPT(Casablance), Kingdom of Morocco. Now he is working as an electronics engineer in the private sector in Bulgaria.

#### To read other interesting DIY projects: click here

# Micro Inverter

By Rohan B. Rebello

February 5, 2018

64140

Advertisement

A simple low-power inverter circuit is described here, which converts 12V DC into 230V AC. It can be used to power very light loads like night lamps and cordless telephones, but can be modified into a powerful inverter by adding more MOSFETs.

## Battery charger circuit

This circuit has a two stage-battery charger with cut-off and battery level indicator and an inverter circuit. Charging circuit is built around IC1 (LM317) as shown below. When mains 230V AC is available, IC1 provides the gate voltage to SCR1 (TYN616) through diode D3 (1N4007). SCR1 starts charging the battery. For output voltage setting preset VR1 may be used.

Battery charger with cut-off circuit

The battery level indicator & inverter circuit is shown below. The battery level checking system is built around transistors T1 and T2 (both BC547) along with some discrete components. When the battery is charged (say, to more than 10.50V), LED1 glows and piezo-buzzer PZ1 does not sound. On the other hand, when battery voltage goes down (say, below 10.50V), LED1 stops glowing and piezo-buzzer sounds, indicating that the battery has been discharged and needs recharging for further use.

## Inverter circuit

Battery level indicator & inverter circuit

The inverter is built around IC2 (CD4047), which is wired as an astable multivibrator operating at a frequency of around 50 Hz. The Q and Q outputs of IC2 directly drive power MOSFETs (T3 and T4). The two MOSFETs (IRFZ44) are used in the push-pull configuration. The inverter output is filtered by capacitor C1.

## Construction & testing

Assemble the circuit on a general-purpose PCB and enclose it in a suitable metal box.

Pin configurations of TYN616, IRFZ44 and LM317

Refer the pin configurations before mounting the components on the PCB. Mount the transformer on the chassis and the battery in the box using supporting clamps. Use suitable heat-sinks for MOSFETs. The circuit can be used for other applications as well by delivering higher power with the help of a higher current rating transformer and additional MOSFETs.

The article was first published in January 2010 and has recently been updated.

Advertisement