- Example Power Plant Projects

Jump to navigationJump to search

Navigation: User Guide -> Example Projects -> Example Power Plant Projects

- Contents

- 1Demand Project with Desuperheaters

- 2Power Plant Example

- 3Rankine Cycle Example

- 4Cogeneration Example

- Demand Project with Desuperheaters

Project Location

This is a Steady State project and is stored at:
..\SysCADXXX\Examples\55 PowerPlant\Demand Example(with desuperheaters).spf

Features demonstrated

- Demand in Pipes and Feeders.

- Using saturated and super-heated steam.

- Desuperheater

- Flash Tank

- Example Stream Report.xls

Brief Description

The project shows an overall view of steam usage in a plant.

- The plant is supplied with a single source of super-heated steam.

- The steam is used in the plant at three different pressures, all requiring saturated steam.

- The saturation is carried out in Desuperheaters after the pressure has been reduced across a Valve. The amount of water added is controlled by the Desuperheater via the Demand logic.

- The steam requirement for each area of the plant is set in the Demand section of the pipe feeding the area.

- A reaction block in each area condenses the steam to water while maintaining the temperature at a constant value. This emulates the conditions in the plant, where the energy from the condensation is taken up with heating requirements.

- Condensate from the higher pressure and temperature steam is flashed in a Flash Tank to recover steam at the next lower temperature steam required. The steam recovered joins up with the fresh steam feed.

- The General Controller sets the temperature and pressure of the feed steam, as well as the required pressures for the HP, MP and LP steam.

A similar project not using the desuperheater process model is also available, see Demand Project

Project Configuration

Steam Supply Feeder

- The SuperHeated_Steam Feeder in this project will provide all the steam demanded by downstream processes.

  - Feed_XPG-1 Tab, Select Demand.On, check that Demand.Max will cover the flowrate range for the project. Increase this value if necessary.

  - Qm_Rqd will represent the minimum value for the steam supply. If this value is higher than downstream requirements, the excess amount is distributed. Recommend using a small number of this field.

  - Define the operating condition and composition.

  - SysCAD will calculate the feed flowrate and display it in the Results:Flow Conditions Qm field.

Desuperheating Water Supply Feeder

- The DesuperHeating WATER Feeder in this project will provide all the water demanded by desuperheaters.

- Set up this unit as per the steam feeder above.

Desuperheaters

- The Desuperheaters are set to achieve Saturated conditions.

  - The pressure is defined by the valve feeding the desuperheaters,

  - DemandConnection is set to General Demand, this together with the WATER feeder put on Demand mode, will auto add just enough water to give the saturated conditions.

  - Compare this with the Demand Project, this eliminates the need for PID + Condensing reactions in the desuperheating section.

Steam Users

- When defining the steam users / steam distribution, it is important to NOT use the SPLITFLOW options in Tanks/Ties. The distribution of steam should be specified in PIPES.

- For Example, for the HP_Steam_Distributor,

  - SplitFlows is NOT selected.

  - Outlet Pipes S009 to S012 have steam demand requirements defined in the Pipe-1 Tab, under Qm_Demand.Rqd field.

  - HP_Steam_Distributor Tie-1 Tab shows a summary table of the stream demand values.

- It is important that EVERY steam user amount is defined, this will allow the calculation of the total feed required.

Included Excel Report

Steam Report.xls - This file includes Steam Diagram and Streams report.

- Power Plant Example

This image has been updated to SysCAD 138 version.

Project Location

This is a Steady State project and is stored at:
..\SysCADXXX\Examples\55 PowerPlant\Power Plant Example.spf

Features demonstrated

- Boiler

- Turbine

- Desuperheater

Brief Description

This is a simple closed loop power plant circuit, with 1 boiler, 5 turbine extraction stages, heat sinks (condensers) and Boiler water feed make up. This project also contains some simple side calculation for Fuel usage (found in the General controller.)

Project Configuration

- Boil Feed Water top up amount balances the losses in the boiler, this is done via the PGM controller.

- Boiler - define final T&P, efficiency and blowdown

- Turbines - define pressure and efficiency. The Steam produced maybe superheated or two phase saturated.

- All heat exchangers are set in fully condensing mode, with Area and HTC defined. The CondenseAll option is selected to unsure all the steam is condensed should the specified area is too small. The actual area required is shown in the TheorArea Field.

- Fuel calculation are done via the PGM controller as a side calculation.

Included Excel Report

None

- Rankine Cycle Example

This image has been updated to SysCAD 138 version.

Project Location

This is a Steady State project and is stored at:
..\SysCADXXX\Examples\55 PowerPlant\Rankine Cycle Example.spf

Features demonstrated

- Boiler

- Turbine

- Desuperheater

- Simple Condenser

Brief Description

This is a simple open loop power plant circuit, with 1 boiler, desuperheater, 2 turbine extraction stages and condenser. Shows the simple steam-plant-cycle and generation of electric power and process steam.

Project Configuration

Desuperheating Water Supply Feeder

- The DesuperHeating WATER Feeder in this project will provide water demanded by desuperheaters.

  - FeederSink Tab, Select Demand.On, check that Demand.Max will cover the flowrate range for the project. Increase this value if necessary.

  - QmReqd will represent the minimum value for the steam supply. If this value is higher than desuperheater requirements, the unit will report an error.

  - Define the water condition and composition.

  - SysCAD will calculate the water flowrate and display it in the Results:Flow Conditions Qm field.

Desuperheaters

- The Desuperheaters are set to achieve a target Final Temperature.

- DemandConnection is set to General Demand, this together with the WATER feeder put on Demand mode, will auto add just enough water to give the required temperature.

Others

- The configuration of Boiler, Turbine and condenser are as per project Power Plant Example

Included Excel Report

None

- Cogeneration Example

This image has been updated to the SysCAD 138 version.

Project Location

This is a Steady State project and is stored at:
..\SysCADXXX\Examples\55 PowerPlant\Cogeneration Example.spf

Features demonstrated

- Compressor

- Boiler

Brief Description

This is a simple cogeneration plant with an air compressor, burner, expander and boiler. Shows the generation of electric power and process steam.

Project Configuration

Most of the configuration of the model is set by the Co_Gen_Control General Controller. The parameters on the three tabs of the controller are described below:

Feeds tab

- The user can specify the Air feed temperature, pressure, N2 and O2 composition and excess air as a percentage of the required air for complete combustion of the natural gas. The controller calculates and sets the flow of air to achieve the specified excess air.

- The user can specify the Natural Gas feed temperature, hydrocarbon, CO2 and N2 composition.

- The Burner Feed Pressure is specified by the user. This sets the air compressor outlet and natural gas feed pressures.

- The user specifies the Boiler Feed Water temperature.

Power tab

- The user specifies the air compressor efficiency, which is passed to the air compressor model.

- The user specifies the expander (modelled by a compressor unit model) efficiency and outlet pressure. The outlet pressure is passed to the expander model while the efficiency is used for power calculations within the controller.

- The user specifies a Target for Power Generation and this becomes the setpoint for the Power Control PID Controller, which varies the natural gas feed flow to achieve the target power.

- The controller calculates the net power generated which takes account of power required for air compressor and the efficiency of the expander. This is the measured value for the Power Control.

Steam tab

- The user can specify the required steam pressure and the pressure drops from the Boiler Feed Water to the Drum and from the Drum to the Steam Pressure. Based on these settings the controller sets the Boiler Feed Water and Boiler Drum pressures.

- The user specifies the boiler efficiency and blowdown which are then passed to the Boiler model.

- The user specifies a target steam mass flow and the boiler feed water mass flow is set based on this target after taking account of the loss due to blowdown.

Others

- The boiler feed water is assumed to be 100% pure water.

- The burner is simulated by a Tie with reactions for the complete combustion of methane, ethane and propane gases with oxygen gas.

Included Excel Report

Seminars & Symposium

Lee, Young Cheol | Kim, Jae Hwan

How to cite this article:

Lee, Y. C. & Kim, J. H. (2002). Project management for power plant construction in Korea. Paper presented at Project Management Institute Annual Seminars & Symposium, San Antonio, TX. Newtown Square, PA: Project Management Institute.

Reprints and Permissions

### Introduction

Currently, Korea has 50 million kilowatts of installed capacity. The capacity forecasted for new power plants that will be constructed in the future is about 37.44 million kilowatts of electricity to meet power demand and the total capacity of all the power plants in Korea is expected to reach 79 million kilowatts of electricity by 2015.

Power generation division of the state-run KEPCO (Korea Electric Power Corporation) was divided into seven companies on April 2, 2001, which was the first step to privatization. While the existing KEPCO is in charge of power transmission and distribution only, one hydro and nuclear power company and five thermal power companies were established to be in charge of power production as KEPCO's subsidiary companies. This paper describes Korea's typical project management regarding control and administration of in-vestments on power plant construction in a large scale.

#### History of Enhancing System for Power Plant Construction

In the 1960s, contracts for design, equipment, and construction were ordered respectively, obtained foreign funds, and managed by foreign companies. During this period, a project manager was appointed for the first time to be in charge of all the projects. The developed method of the construction project management was applied to Kunsan thermal power plant, 75 thousand kilowatts (2 units), in Korea, which was managed and administered by a foreign company.

From the 1990s up to the present time, the method of piece-meal order was carried out by KEPCO, which reflects the merit of a turnkey order based upon KEPCO's experience in construction management. This method involved separate design, equipment procurement and construction, wherein the design and the construction were performed by different contractors and material and equipment were procured from different suppliers. This method resulted in a number of advantages such as reduction of total project costs and project management personnel. Also, in a construction or installation standpoint, with a firm fixed contract price, which equates to 70% of the total price, it reduces the possibility of construction cost increases due to project uncertainties. It means that owner could minimize his degree of risk due to cost overruns.

#### Necessity of Project Management

In general, project management for power plant construction is set to have functions such as establishment of project basic plans to enable construction work to be performed properly in accordance with quality requirements within budget and schedule, preparation for project organization and management including control and adjustment of division of responsibility. Essentially, a large capacity power plant construction needs considerable amount of investment, along with a large manpower size throughout the whole construction period. Therefore, the division of responsibility during the basic plans stage, design stage, project execution and project closing has to be managed systematically and efficiently. To achieve this goal, the project manager (general manager of construction department) establishes and runs a construction management system to monitor, analyze, and evaluate project current status. The construction management system contains a procedure or computerized system that facilitate a more effective project management program in terms of schedule, cost, equipment material, drawing documentation, project numbering system and integrated reporting system, etc.

#### Project Management Basic Policy

Generation company (GENCO), which is an owner and client, is mainly in charge of project management framework. The general manager plays an important role as the chief of construction department at the head office. He is in charge of overall work of the project. Actual construction work is managed by the site manager. The related contractors establish and run their own project management system based on client's system.

The owner's primary work items at the head office are:

•  Establishment of construction basic plans and detailed action plans

•  Establishment of guidelines for project management

•  Procurement for architecture engineering, main equipment, balance of plant and construction, etc., and post-contract work

•  Setting up a computerized project management system on construction schedule, construction cost, equipment material, drawing, documentation and project numbering system, etc.

•  Obtaining government approval.

Exhibit 1. Schedule Control System

The owner's primary work items at the job site are:

•  Operation of project management system

•  Obtaining local government approval

•  Quality control for manufacture and erection

•  Construction control and supervision

•  Safety and environmental management

•  Start-up or commissioning

Related contractors’ work items are:

•  Establishment of project execution plan and implementation

•  Establishment of project management system and operation

•  Establishment of human resources, construction machinery mobilization and implementation

•  Reporting monthly project progress to the owner.

#### Standard Project Management Systems

Standard project management systems are being utilized for 500MW supercritical coal fired plants in Korea, which are as follows:

•  Schedule control systems including procedures, software programs and user's manuals

•  Cost control systems including procedures, software programs and user's manuals and cost database software programs

•  Material control systems including procedures, software programs and user's manuals

•  Document control systems including procedures, software programs and user's manuals

•  Project numbering system including procedures

•  Computerized system including construction management software

•  Integrated reporting systems including procedures, software programs and user's manuals.

#### Project Execution Process

##### Establishment of Construction Basic Plans for Power Projects

The Korean government prepares the basic plans for the stability of supply and demand of electricity in the country. Based upon the plans, the generation company selects the most feasible location for the new power plant, which is classified as the highest priority item among the suggested locations. Once this has been accomplished, construction basic plans are prepared by an expert from GENCO's construction department, and authorized by the board of directors to be launched as a project. The basic plans include: location, installed capacity, construction period, site settlement, yearly investment, financing, fuel supply and environmental conservation.

##### Establishment of Detailed Action Plans for Construction Project

Setting up of procurement method, contract award, construction permit from the government, and construction schedules. Milestone schedules usually include: site improvement, power building excavation, foundation concrete, structural steel erection, boiler pressure part start, power receiving, boiler hydrostatic test, initial firing, steam admission to turbine, initial synchronization and commercial operation.

Exhibit 2. Progress Rate Calculation

##### Evaluation of Environmental Effects

When the construction plans of a power plant of more than 10,000 kilowatts is prepared, it is performed during the feasibility study stage to mitigate environmental effects during construction and operation periods. It also includes review of reducing effects to environment, gathering of residents’ opinion through public hearings, final evaluation report and conference with the Environmental Protection Agency.

##### A/E (Architectural Engineering)

During the basic design stage, GENCO makes a decision about the basic concept and design criteria, equipment types and capacity, along with the establishment of design margins or automatic control systems range, which is prepared by the architectural engineering contractor. During the detailed design stage, GENCO finalizes drawings and design documents based on optimization methods of the basic design concepts.

##### Contract for Equipment Purchase

Equipment purchase accounts for 30% of the total power plant construction cost. According to financial sources, procurement of equipment is classified as “domestic” and “foreign.” GENCO's head office in Seoul handles the procurement from foreign countries, as these material and equipment are imported from outside, which is more economical in terms of efficiency and effectiveness. In accordance with the conditions of the site arrangement and design criteria, technical specifications are prepared. General design conditions include: general description, power plant outline, site conditions, environmental design limits, utility resources, quality of industrial water and sea water.

Technical specifications contents include: division of responsibility for equipment supply, codes and standards, operating conditions, design and manufacturing characteristics.

#### Schedule Control Practice

Integrated project schedule control is the core of the project management system, which is identified in various fields such as design, procurement, construction, and commissioning. The objective of the schedule control is to ensure that the project is consistently on schedule to avoid cost overruns caused by delays.

Schedules are used to plan and depict practical, time-phased, hierarchical activities and events, which include activities, logical relationships, durations, resource requirements and constraints in order to maintain a key-milestone and limited time schedule with hierarchy such as project milestone schedule, summary schedule, construction control schedule and detailed schedule as shown in Exhibit 1.

Level 1, which is the highest level (project milestone schedule) depicts major events associated with engineering, procurement, construction and start-up during the entire project, which is also a project master schedule. Level 2 (EPCS Summary schedule) contains minimal logical relationship, which is utilized by prime contractors as the highest level schedule. Level 3 (Construction control schedule) is an integrated schedule utilizing the critical path method. Level 4 (Detailed schedule) is developed and controlled by major participating contractors based on the Level 3 schedule.

Level 1 consists of 50–60 line items that depict major milestones, invitation to bid, purchase order award and initial delivery. It facilitates a higher level of management to monitor and manage the whole project properly and typically contains work items as follows:

•  General: general arrangement, site improvement, coal yard, raw water supply facilities, access road, harbor facilities, ash storage area, community complex and service building

•  Boiler: foundation, structure, boiler and auxiliary system, piping and instrumentation and chimney

•  Turbine and Control: foundation, structure, base mat and turbine generator pedestal, turbine generator and auxiliary system, feed water system, condenser and accessories, condensate system, cooling water system, crane, piping and instrumentation

•  Auxiliary: ash handling system, electrostatic precipitator, water treatment system, coal handling system, fuel oil system, flue gas desulphurization system, waste water treatment system, compressed air system, auxiliary boiler and accessories, emergency generator system, fire protection system, HVAC, intake and discharge facilities and circulating water system structure

•  Electrical: electrical equipment, power transformer, gas insulated substation, switchgear, motor control center, UPS and DC system, tray and conduit, cable, other electrical facilities

•  I&C: control and computer facilities, balance of plant instrumentation and control.

Exhibit 3. Civil Construction Package Examples

Exhibit 4. Control Points Examples

Level 2—Engineering summary schedule is identified according to the design work process and contains 500 work items. Procurement summary schedule comprises equipment (boiler, turbine and BOP) illustrating the invitation to bid issue, award purchase order, receipt of vendor drawings, FOB date for offshore items and initial site delivery. Construction summary schedule is a time scaled network according to building and field such as civil, architecture, mechanical and electrical design.

Level 3 is a construction control schedule that represents detailed planning through the logic network and utilized by schedule controller on site to analyze the current performance status of the schedule. The schedule controller provides data needed for required government reporting and in-house reporting.

#### Examples of Progress Rate Calculation

The progress rate on project status reports is classified based upon managed area such as EPCS, which has weighted values of 20% for engineering, 30% for equipment procurement, 45% for construction and 5% for start-up. Criterion on value calculation based on the managed area is as follows:

•  Engineering and start-up man-hours

•  Equipment procurement cost

•  Contract price, erection constraints and loaded resources for construction.

For example, weighted value for construction area consists of 32% for civil work package, 19% for architecture, 38% for mechanical and electrical, and 11% for I&C which amounts to 100% as shown in Exhibit 2.

Regarding construction progress status reports, the progress rate is classified based upon the construction package as shown in Exhibit 3.

There are various methods in calculating the percent complete which are 0-100, level of effort, 50:50 and design quantity of material or control points, etc. Bulk material is managed on the basis of quantity, and individual material is handled through control points as shown in Exhibit 4. Status reports reflecting erection completion are commonly used to remunerate earned values on a monthly basis.

### Summary

Through the Project Management for Power Plant Construction in Korea, Korea Western Power Co., Ltd. (WP) introduced the Korean project management system commonly used in power generation companies. WP also outlined the project execution process and explained the schedule control methodology applied to large capacity coal fired power plants. To privatize KEPCO's exclusive ownership, the corporation was divided into six small companies in 2001, as a result these groups became competition against each other, which in effect increased the efficiency and competitiveness. It is necessary for a utility company to cut down the total project cost, as it would also lower the generation cost. One of the ways to cut down the construction cost is to effectively utilize a project management system to meet the target schedule and to be within the target budget.

This material has been reproduced with the permission of the copyright owner. Unauthorized reproduction of this material is strictly prohibited. For permission to reproduce this material, please contact PMI or any listed author.

Proceedings of the Project Management Institute Annual Seminars & Symposium
October 3–10, 2002 • San Antonio, Texas, USA

ADVERTISEMENT

ADVERTISEMENT

## Related Content

- 5 October 2020

### Project Management Institute Launches Its Ninth Chapter in India the PMI Gujarat Chapter

Project Management Institute Launches Its Ninth Chapter in India the PMI Gujarat Chapter

- Complexity, Decision Making, Organizational Project Management, Procurement Management 30 September 2020

Sponsored Research

### Reinventing Megaproject Delivery Models

By Denicol, Juliano Megaprojects are usually proposed by the public sector as a reflection of the government delivering a new physical asset to address a necessity of the society, improve living conditions, foster…

- 24 September 2020

### stc Announces Strategic Partnership with Project Management Institute (PMI)

stc Announces Strategic Partnership with Project Management Institute

- 2 September 2020

### PMI Community Members Take the TED Mainstage to Share Big, Bold, Creative Ideas at Virtual Event

PMI Community Members Take the TED Mainstage to Share Big Bold Creative Ideas at Virtual Event

- 19 August 2020

### Comedian Trevor Noah and Host Tamron Hall Lead PMI® Virtual Experience Series Event on 25 August

Comedian Trevor Noah and Host Tamron Hall Lead PMI Virtual Experience Series Event on 25 August

ADVERT